## . (hidden)
This program was designed for Gustavo Adolfo Velasquez in November 20, 2007, All copyright protected
| Pressure psig | BTU/Lb |  |  | Altitud fts | Altitud Mts | Presion PSI | Presion HG
| 0 | 970 |  |  | 0 | 0 | 14.6953 | 29.92
| 5 | 961 | PSIG | 30 | 1000 | 304.8037 | 14.1747 | 28.86
| 10 | 953 |  |  | 2000 | 609.6074 | 13.6639 | 27.82
| 15 | 946 | BTU/Lb | 929 | 3000 | 914.4111 | 13.1728 | 26.82
| 20 | 939 |  |  | 4000 | 1219.2148 | 12.6914 | 25.84
| 25 | 934 |  |  | 5000 | 1524.0185 | 12.2248 | 24.89
| 30 | 929 |  |  | 10000 | 3048.0371 | 10.108 | 20.58
| 35 | 924
| 40 | 920
| 45 | 916
| 50 | 912
| 60 | 905
| 70 | 898
| 80 | 892
| 90 | 886
| 100 | 881
| 110 | 875
| 120 | 871
| 130 | 866
| 140 | 861
| 150 | 857
| 175 | 847
| 200 | 837
| 225 | 828
| 250 | 820

## Read First
Cost of Energy in Steam Traps Failing Open
How use the Calculator
Steam traps are a fundamental component of any steam system for maximum performance and
efficient energy use.
Steam traps operate using mechanical, thermostatic or thermodynamic principles, but regards which
principle they are using only fails in two ways; Open or Closed. A Open trap allow steam waste with its
consequences in fuel consumption. A closed trap in the other hand keep the condensate inside the
system with water hammer risk among the other consequences.
It is clear then that steam traps must work efficiently and be reliable. Is only one way to keep the
steam system working as it is intended; doing steam traps inspection periodically.
Results from steam traps inspection are not always easy to quantify, but using some principles of
fluid mechanics and heat transfer it is possible get the real cost of energy wasted.
This Calculator has been design to help the inspectors quantify the cost of the steam traps which
fails in OPEN position allowing steam go through.
Use this data sheet is straight forward exercise but results are as good as the information load in
green cells
The information MUST BE expressed in the same units as it is requested, so to help those users who
have the information in different units, the calculator has a conversion tool and a atmospheric pressure
finder according to your localization over the sea level .
The orifice size for each trap is provided for the manufacturer and usually its units are inches, however
for ISO units also the calculator provide a easy tool to change units to Imperial.
The cost of fuel can be provide for your account department but again must be expressed in dollar
per million BTU.
The result is the cost of the fuel used in the steam wasted for the particular steam trap open. You
should do the same exercise for each and every trap inspect and found open.

## Energy Cost
Cost of energy in steam traps failing open
| Pressure gauge in the steam trap |  |  | psig
| Local atmospheric pressure |  |  | psi
| Steam trap orifice diameter |  |  | Inches
| Boiler annual operation time |  |  | Hours
| Boiler efficiency |  |  | %
| Cost of fuel per million BTU |  |  | $
| Annual cost per open steam trap |  | #N/A | $
Conversion Units Tool
|  | bars | 0 | psi
|  | inches | 0 | inches
| 0 | mm | 0 | inches
| 0 | Kilo Calories | 0 | BTU
Finding atmospheric pressure with altitude
| Altitude over sea level |  | 0 | meters
| Atmospheric pressure |  | 14.595 | psi
SDT North America is not liable for any use give above results